## Slide 1
Cassette VAVE activities
Cassette VAVE activities
Total: $257.76
Task Name
Savings
End
Status
CAP Tube testing - MT
$28.00
9/4/2026
In Progress
Check valve removal
$5.00
8/21/2026
Not Started
S/M - 1 (Removing parts/clamps from design)
$7.50
8/3/2026
Completed
S/m - 2 (Control box redesign, evap shroud,
compress base, cond. shroud)
$30.00
10/7/2026
In Progress
New enclosure for 2.0 (Molded foam/ Sm/ gasket)
$27.00
10/30/2026
In Progress
Aluminum coil
$30.00
2/1/2027
In Progress
Cheaper Carel controller
$15.00
9/16/2026
In Progress
Task Name
Savings
End
Status
Tube on drip tray
$0.00
7/24/2026
In Progress
Harness design
$20.00
9/17/2026
In Progress
Evap/ Condenser fan - 3 qty
$42.00
8/28/2026
In Progress
Pallet - CArdboard design
$10.00
9/28/2026
In Progress
Tariff - MT
$43.26
6/15/2026
REALIZED
Tariff - LT
$44.59
6/15/2026
REALIZED
Notes: Source: VAVE-DG 2.0 workbook and latest user-provided screenshots. Level 2 and Level 3 headings retained as slide headlines/rows.

## Slide 2
Case VAVE activities
Case VAVE activities
Total: $78.29
Task Name
Savings
End Date
Status
Plastic Deck Pans
$26.65
9/18/2026
In Progress
Simplify Raceway
$3.07
8/7/2026
In Progress
Case power cord
$5.49
9/1/2026
In Progress
10Amp Breaker
$32.56
8/11/2026
In Progress
Simplify Under Door Support
$1.48
8/7/2026
In Progress
Reduce Qty of Canopy Foam Backers
$5.27
8/7/2026
In Progress
Remove Drain
$3.77
8/12/2026
In Progress
Notes: Source: VAVE-DG 2.0 workbook and latest user-provided screenshots. Level 2 and Level 3 headings retained as slide headlines/rows.

## Slide 3
VAVE Savings Summary
Case / Model
Potential
Realized
Remaining
% Realized
RMN5MA
$597.50
$86.52
$510.98
14.5%
RMN4MA
$594.10
$86.52
$507.58
14.6%
RMN3MA
$590.70
$86.52
$504.18
14.6%
RMN2MA
$322.50
$43.26
$279.24
13.4%
RLN5MA
$859.30
$133.77
$725.53
15.6%
RLN4MA
$596.80
$89.18
$507.62
14.9%
RLN3MA
$593.40
$89.18
$504.22
15.0%
RLN2MA
$323.90
$44.59
$279.31
13.8%
Updated values based on latest VAVE calculations. Total row intentionally removed.
Notes: Source: VAVE-DG 2.0 workbook Summary tab. Circled duplicate open-activity section removed and replaced with all-model realized savings summary.

## Slide 4
Case + MB Cost Summary
Case / Model
Case + MB Cost - Current
Case + MB Cost - Aug,26
Case + MB Cost - Dec, 26
Case + MB Cost - Feb,28
RMN5MA
$6,738.09
$6,626.75
$6,204.28
$6,144.28
RMN4MA
$6,335.50
$6,224.16
$5,801.69
$5,741.69
RMN3MA
$5,935.16
$5,823.82
$5,401.35
$5,341.35
RMN2MA
$3,927.53
$3,866.95
$3,621.48
$3,591.48
RLN5MA
$8,698.13
$8,532.04
$7,932.57
$7,842.57
RLN4MA
$6,667.58
$6,553.58
$6,131.11
$6,071.11
RLN3MA
$6,198.86
$6,084.86
$5,662.39
$5,602.39
RLN2MA
$4,123.70
$4,061.79
$3,816.32
$3,786.32
Updated values based on latest VAVE calculations. Total row intentionally removed.

## Slide 5
Dispatch data per store installation week
All issues included
0
5
10
15
20
25
Total Dispatches
Store installation week
6
3/2
9
3/9
24
3/16
16
3/23
4
3/30
13
4/6
18
4/13
6
4/20
6
4/27
7
5/4
2
5/11
5
5/18
4
5/25
2
6/1
1
6/8
6
6/15
1
6/22
4
6/29
Root Cause
Ref. leak / Low charge
Door Torque
Drain tube blocked
Wrong / Loose wiring
Door issue
Comm line Installation Problem
High Store RH
Enclosure Seal
Component Failure
Defrost Sync
False Alarm
Incorrect Program
Overstocking
Case End Seal
Return Air blocked
Unidentified air leak
Freedom
Heavy case load
DG Installation issue
Unknown
Program change - Hussmann
Total issues: 134
DISPATCH BREAKDOWN: TOTAL (FALSE)
STORE CONNECT - 65 (6)
FEXA - 47 (6)
RPM - 2 (1)
ENG - 0 (0)
OTHER - 7 (0)

## Slide 6
June + July issues by root cause
0
10
20
30
26
Doors
9
False Alarm
5
Unknown
4
Communication
problem
4
DG
Installation
issue
4
High
Store RH
2
Component
Failure
2
Drain
tube
blocked
2
Ref. leak /
Low charge
2
Wrong /
Loose wiring
1
Incorrect
Program
1
Overstocking
Number of Issues
Root Cause Category
Root Cause
Doors
False Alarm
Unknown
Communication problem
DG Installation issue
High Store RH
Component Failure
Drain tube blocked
Ref. leak/ Low charge
Wrong / Loose wiring
Incorrect Program
Overstocking
Doors = Door Torque + Door issue
Total June + July rows with issues: 61

## Slide 7
June + July issues by root cause (After clean point)
0
10
20
30
Number of Issues
Root Cause Category
3/26
Doors
3/9
False Alarm
0/5
Unknown
1/4
Communication problem
0/4
DG Installation issue
0/4
High Store RH
0/2
Component Failure
1/2
Drain tube blocked
2/2
Ref. leak / Low charge
2/2
Wrong / Loose wiring
1/1
Incorrect Program
1/1
Overstocking
Bar Split
Before / at clean point
After clean point
Root Cause
Doors
False Alarm
Unknown
Communication problem
DG Installation issue
High Store RH
Component Failure
Drain tube blocked
Ref. leak / Low charge
Wrong / Loose wiring
Incorrect Program
Overstocking
Total June + July rows with issues: 61

## Slide 8
Root Cause Deep Dive – Doors
New clean point date
7/17/2026
After clean point issues
3
Total category issues
26
Issue category
Doors
Issue Break down
ISSUE QTY
Doors losing Torque - 8
Doors not closing/ not closing overnight 12
Door gasket issues 3
Torsion rod failure 1
Door heater/ Door frame heater issues 2
Engineering Proposed Solution / Solutions
RESOLUTION TIMELINE
Installation sign off sheet for RPM 7/9/2026
Engineering Instruction label on the glass door 7/17/2026

## Slide 9
Root Cause Deep Dive – False Alarm
New clean point date
7/24/2026
After clean point issues
3
Total category issues
9
Issue category
False Alarm
Issue Break down
ISSUE QTY
Cancelled dispatch – Case pulled back down 3
FEXA alarm – Tech found nothing wrong with case 4
Store connect alarm – Cleared itself when tech reached 2
Engineering Proposed Solution / Solutions
RESOLUTION TIMELINE
Checking if control logics could be modified 7/24/2026
Lab testing to figure out case breaking points 7/24/2026

## Slide 10
Root Cause Deep Dive – Refrigerant leak
New clean point date
TBD
After clean point issues
2
Total category issues
2
Issue category
Refrigerant leak
Issue Break down
ISSUE QTY
Potential TXV leak – under investigation 1
Unknown – Waiting for cassette to be returned 1
Engineering Proposed Solution / Solutions
RESOLUTION TIMELINE
Will send TXV to Sporlan for further investigation TBD

## Slide 11
Root Cause Deep Dive – Drain tube blocked
New clean point date
7/17/2026
After clean point issues
1
Total category issues
2
Issue category
Drain tube blocked
Issue Break down
ISSUE QTY
Drain tube blocked because of excess foam 2
Engineering Proposed Solution / Solutions
RESOLUTION TIMELINE
Low expansion foam implementation 7/17/2026
Plastic drain tube cover (Investigating) 7/31/2026